- EED Reporting

This appendix presents a template and example of an energy reporting format aligned with the EU Energy Efficiency Directive (EED), especially following the recast Directive (EU) 2023/1791, which introduces mandatory reporting for data centres with an IT load of over 500 kW.

ENERGY REPORTING TEMPLATE

Directive: EU Energy Efficiency Directive (Recast 2023/1791)

Target audience: Data centers >500 kW installed IT load

Reporting frequency: Annually (since 2025), by 15 May for the previous calendar year

Reporting platform: National authorities or central EU repository (e.g. EU EPREL equivalent or national energy agency portals)

SECTION 1: GENERAL INFORMATION

| Field | Value |
| --- | --- |
| Data Center Operator Name | ExampleCloud Services BV |
| Address | Science Park 101, 1098 XG Amsterdam, Netherlands |
| Country | Netherlands |
| Reporting Year | 2024 |
| EED Reporting ID | NL-DC-042 |
| Installed IT Load (kW) | 750 kW |
| Operational Floor Area (m²) | 1,800 m² |
| Reporting Contact | energy.compliance@examplecloud.eu |

SECTION 2: ENERGY USE AND PERFORMANCE INDICATORS

| Indicator | Value | Notes |
| --- | --- | --- |
| Total Annual Energy Consumption (MWh) | 6,200 MWh | Includes all electricity use (IT, cooling, lighting, etc.) |
| IT Equipment Energy Consumption (MWh) | 3,800 MWh | Measured via intelligent PDUs |
| Power Usage Effectiveness (PUE) | 1.63 | Target to reach 1.4 by 2026 |
| Renewable Energy Share (%) | 82% | Mix: On-site solar + green PPA |
| Energy from District Heating/Cooling (MWh) | 0 MWh | N/A |
| Energy Reuse (MWh) | 600 MWh | Waste heat reused in adjacent office building |
| Waste Heat Reuse Efficiency (%) | 9.7% | Of total facility energy |

SECTION 3: WATER AND COOLING

| Indicator | Value | Notes |
| --- | --- | --- |
| Water Usage for Cooling (m³/year) | 900 m³ | Evaporative cooling towers |
| Water Usage Effectiveness (WUE) | 0.24 L/kWh | Calculated based on total energy use |
| Cooling Method | Hybrid: Free cooling + evaporative | Liquid cooling in testing phase |

SECTION 4: RESOURCE MANAGEMENT & IMPROVEMENTS

| Measure | Status | Description |
| --- | --- | --- |
| ISO 50001 Certification | Achieved (2023) | Energy management system implemented |
| Dynamic IT Load Scheduling | Partial | Energy-aware orchestration under pilot |
| Cold Aisle Containment | Full | Implemented across all server rooms |
| Hardware Refresh Plan | In Progress | Low-power servers and accelerators to replace legacy hardware (by 2026) |
| E-waste Management | Compliant | ITAD program with zero landfill policy |

SECTION 5: TARGETS AND ROADMAP

| Target | Deadline | Progress |
| --- | --- | --- |
| Reduce PUE to 1.4 | End of 2026 | Efficiency projects underway |
| Reach 100% renewable energy use | 2027 | Expanding PPA scope |
| Achieve Net-Zero (Scope 1 & 2) | 2030 | Internal roadmap approved |
| Recover 15% of waste heat | 2026 | Collaboration with local district heating grid |

ANNEXES

- Energy bills and renewable energy certificates

- PUE measurement methodology and logs

- ISO 50001 certificate copy

- Water usage invoices/logs

- Emission calculations (Scopes 1 & 2)

- Cooling system specifications